## Ground mount
Operation & Maintenance Plan - Rice Road Solar Project |  | Planned Maintenance Frequency
Ground Mount Scope of Work |  | Recommended Servicing
1. Modules
1.1 | Inspection of modules for anomalies and damage | Annually
1.2 | Verify module cleanliness | Annually
1.3 | Visually inspect array for damaged or loose modules | Annually
1.4 | Inspect module clamping methodology particularly for loose fastener, bolt/nut, torque check | Annually
1.5 | High level of inspection front and back sheet (debris, crack, holes, damages, burn marks, output performance) | Annually
1.6 | Top glass inspection for spots, blemishes, signs of arcing in circuitry, bonding of frame to glass, discoloration, cracks, chips, shattered glass, etc. | Annually
1.7 | Back sheet inspection for spots, blisters, burn throughs, discoloration, delamination, bubbles, cracks/scratches, etc. | Annually
1.8 | Identifying cracks and other defects/damage on PV module cables, connectors, junction box. | Annually
1.9 | Inspect module junction boxes on subset of array for issues with adhesives (loose/brittle, fell off etc.), wire management (+/- connectors, seal) | Annually
1.1 | Module washing | On Demand
2. Array & Racking
2.1 | Inspection of array for anomalies and damage | Annually
2.2 | Inspection of racking, piling, hardware and other components for abnormal wear, corrosion/rust, soil erosion, etc. | Annually
2.3 | Check for ground continuity between frames, racking structure | Annually
2.4 | Check for corrosion between copper wires, PV frames and galvanized steel racking structure | Annually
2.5 | Posts - Visual inspection of post settling | Annually
2.6 | Purlin - Visual inspection on bent purlins, attachment to pivot arm | Annually
2.7 | Fasteners - Inspected annually - retorqued if necessary | Annually
2.8 | Wiring/Strings - Inspect for loose or damaged wiring | Annually
2.9 | Racking - Inspect for bent or deformed structural members | Annually
2.12 | Identifying shading issues from surrounding objects | Annually
2.13 | Visual inspection of frost heave | Annually
3.Ballasted Racking System
3.1 | Visual inspection of the ballast blocks and mounting hardware | Annually
3.2 | Inspection for any signs of wear and tear, weather damage, cracks, deterioration or movement | Annually
3.3 | Inspection of stone levelling pad for runoff | Annually
3.4 | Inspecting shifting or settling of ballast blocks that may affect system stability and performance | Annually
4. Conduits, Cable trays & Home runs
4.1 | Visual inspection of home-run cables (PV, DC, AC) to inverters and arrays, CB’s, RCB’s & disconnects | Annually
4.2 | Visual inspections of conduit & cable trays | Annually
4.3 | Wire insulation in good conditions (not scuffed or broken) | Annually
4.4 | Inspecting PV wiring for cuts, strains or any interfering with module installation, tracker axis of rotation | Annually
4.5 | Inspecting and securing loose conductors exposed to direct sun/rain, touching the ground, insulation issues, mechanical protection, stress etc. | Annually
4.6 | Inspect flexible conduit and homerun wires between moving parts (torque tubes/ modules/ etc.) for wear from cyclic motion | Annually
5. Combiner & Recombiner Boxes
5.1 | Visual internal and external inspection for labelling, moisture entry, rodents & overall cleanliness | Annually
5.2 | Verify Fuses, breakers and surge suppression are in good conditions | Annually
5.3 | Inspection of disconnect sealing, Lubrification Hinges | Annually
6. Inverters
6.1 | Visual internal and external inspection of safety labelling, limacoid, heat sinks, moisture entry, rodents & overall cleanliness | Annually
6.2 | Check for Alerts/Alarms on inverter screens | Annually
6.3 | Enclosure is free from damage, all weather seals are intact, doors and latches operate properly | Annually
6.4 | Inverter AFCI (Arc Fault Circuit Interrupter) Status | Annually
6.5 | Vacuum all debris/dust inside inverter | Annually
6.6 | Check all electrical terminals and fuses | Annually
6.7 | Verify inverter communications | Annually
6.8 | Voc & Isc 33% of strings | Annually
6.9 | Confirm area around inverter is free from vegetation | Annually
6.1 | Inspection of inverter forced ventilated cooling systems including filter screens, heat sink fins or similar devices. | Annually
6.11 | Check inverter surge arrestors, surge guards and similar power filter devices | Annually
6.12 | Operate all inverter AC and DC disconnect switches. Validate inverter response to shut down and proper startup. | Annually
7. DAS - SCADA
7.1 | Inspection of SCADA & Monitoring System Equipment | Annually
7.2 | Inspect Weather Station | Annually
7.3 | Ensure sensors are oriented correctly & cleaned | Annually
7.4 | Ensure monitoring data is calibrated with portal and communicating effectively | Annually
7.5 | Clear inside of enclosure of dust, debris, insects, etc. | Annually
7.6 | Wires are landed and secured properly within DAS and modem enclosures | Annually
7.7 | Verify no moisture ingress in enclosures, seal as necessary, and ensure any water or moisture is dried out | Annually
8. Disconnects & Switchboards
8.1 | Inspection of all conduits, cabling, grounding, Inspect for visible damage, broken wire strands, damaged insulation on cable connections | Annually
8.2 | Megger switchboard Insulation #1 - Prior to Cleaning | Annually
8.3 | Visual inspection of disconnects & connections. Review for overall cleanliness, moisture entry, damage, missing labels/limacoid | Annually
8.4 | Cleaning - Remove dust/debris from busbars, connections, supports & enclosure surfaces | Annually
8.5 | Megger switchboard Insulation #2 - Post Cleaning | Annually
8.6 | Insulation - Busbars, Bus Supports, Bus Shields, Insulating Barriers visually checked for damage | Annually
8.7 | Circuit Breakers - Inspect for signs of discoloration, overheating, damage. Exercise operating mechanism. | Annually
8.8 | Visually inspect switching mechanism and fuse connections of DG's | Annually
9. Transformer
9.1 | General - Inspect area for stored tools/materials/debris. Listen for steady hum and no abnormal noises. | Annually
9.2 | Exterior Surfaces - Inspect for tampering, battered metal, gouges, damages | Annually
9.3 | Paint/Protective Coatings - Inspect for scratches or weathering, touch ups required | Annually
9.4 | Tank Leaks - Inspect exterior/base for signs of leakage | Annually
9.5 | Pad - Verify pad is not damaged and has not tilted | Annually
9.6 | Nameplates - Inspect for proper nameplates and abnormal/unexpected fading | Annually
9.7 | Unusual Odors - Inspect for smell of fluid or burning | Annually
9.8 | Gauges & Controls - Check for proper operation | Annually
9.9 | Equipment Leaks - Inspect drain cocks, plugs, fuse mounting, and switches for insulating liquid leakage. | 1 Year after Installation, subsequently every 3 years
9.1 | Dielectric Fluid Level - Check Dielectric fluid level gauge
9.11 | Fusing - Inspect fuses
9.12 | Bushings - Check condition of HV & LV bushings for dirt, breakage
9.13 | Pressure Relief Valve - Check for dirt, debris, operation
9.14 | Lightning Arrestors - Check for damage/breakage and tight ground connections
9.15 | Dissolved Gas Analysis - Take Oil Sample to check dissolved gas levels (third party testing)
9.16 | Insulation Resistance Test
9.17 | Turns Ration Test (TRT)
9.18 | Power Factor Test (Overall, Arrestors, Bushing, Windings)
9.19 | Excitation-Current Tests
9.2 | Winding Resistance Test
10. Thermal Imaging
10.1 | Thermal Images of Inverters (AC/DC) | Annually
10.2 | Thermal Images of AC Panel board/Combiners | Annually
10.3 | Thermal Images of main breakers, disconnects, bus & Cable connections (Incoming & Outgoing) | Annually
10.4 | Provide a report outlining thermal and torquing Anomalies detected | Annually
11. Medium Voltage
11.1 | Inspect medium voltage overhead lines | Annually
11.2 | Check the integrity of guywires | Annually
11.3 | Inspect integrity of the poles | Annually
11.4 | Inspect overhead lines for tree clearance | Annually
12. General Site Maintenance
12.1 | Mowing low grow pollinator grass, general vegetation and weed control inside and outside the system | On Demand
12.2 | Replace dead or dying trees or shrubs | On Demand
12.2 | Collect and dispose of trash and other debris inside and outside the system | On Demand
12.3 | Note presence of vegetation and advise need for removal | Annually
12.4 | Access road clear of debris & in good condition | Annually
12.5 | Snow Removal | On Demand
12.6 | Visually inspect signage, resecure or replace as necessary | Annually
12.7 | Inspect fence surrounding array for any damage or erosion issue | Annually
12.8 | Visually inspect fence for any sign of ingress or compromise | Annually
12.9 | Trim landscape screening hedge-row to 12 foot maximum height | Annually
12.11 | Check the integrity of access gate, gate hasps, padlock & lockbox | Annually
12.12 | Provide Site photos in Maintenance Report | Annually
System Owner will be responsible for conducting preventative maintenance annually per schedule above and corrective maintenance as needed. Systems are monitoring 24/7 with Abundant Solar Power's Operation & Maintenance Asset Management team. Solar O&M actvities will not impact the day to day operations of any active agricultural activies on the property. To reach the O&M Team, please contact: Faiq Khan Asset Manager 647-581-5866 faiq.khan@solarbankcorp.com